## Slide 1: Increasing the output of Solar Cell Using Double Reflectors
Domestic Manufacturing: Experience, Challenge, Opportunities

## Slide 2: Increasing the output of Solar Cell
Increasing the INTENSITY of Radiation
Increasing the SURFACE of SOLAR CELL.

## Slide 3: PV with Double Reflectors
Borrowing the idea of a solar cooker.

## Slide 5: Location of measurement

## Slide 6
PV Module

## Slide 7
Fluke 337 True RMS Clamp Meter
Fluke 73 Series Multimeter
Tang Ampere Kyoritsu Kew Snap 2033
Kompas
Pengukur Suhu Raytek PM Plus

## Slide 8: Angle of Reflectors

## Slide 9: Angle of the sun-shine
March 21 & June 21

## Slide 10: Setting the Angle of Reflectors
Microcontroller ATMega8 is used to generate output signal to trigger the motor driver that moves the motors of the reflectors to position itself in its correct angle.
There are two option of operation being used in this plant.
Open loop system, where the angles of the reflectors are calculated based on the input of the date and location of the plant.
Closed loop system, where the reflectors are moving, looking for the best angle by itself.

## Slide 11: Block Diagram of the control system
Real Time Clock (RTC)
-Controller
Output: Angle of Reflectors
Input Date & Location
Sensors Voc and Isc
Solar Cell

## Slide 12: Closed Loop Operation
Sensors pick up the value of Voc and Isc
Power is calculated using:

## Slide 13: Supporting Circuits
Signal Conditioner for Voc measurement

## Slide 14: Supporting Circuits
Signal Conditioner for ISC measurement

## Slide 15: The Result at 9.00 am (Dec 2009)
Angle N (°) | Angle S (°) | Temp (°C) | VOC (V) | ISC (A) | MPP (W) | Sky
0 | 0 | 41 | 20.1 | 2.26 | 36.74 | bright
10 | 0 | 41 | 20.07 | 2.38 | 38.62 | bright
20 | 0 | 41 | 20.04 | 2.45 | 39.69 | bright
30 | 0 | 41 | 20.01 | 2.45 | 39.61 | bright
40 | 0 | 41 | 19.95 | 2.45 | 39.46 | bright
50 | 0 | 41 | 19.88 | 2.45 | 39.32 | bright
60 | 0 | 41 | 19.95 | 2.66 | 42.85 | bright
70 | 0 | 41 | 20.04 | 2.92 | 47.30 | bright
80 | 0 | 41 | 19.95 | 2.52 | 40.59 | bright
90 | 0 | 41 | 19.88 | 2.52 | 40.44 | bright

## Slide 16: The Result at 9.00 am (Dec 2009)
Angle N (°) | Angle S (°) | Temp (°C) | VOC (V) | ISC (A) | MPP (W) | Sky
70 | 10 | 41 | 19.79 | 2.96 | 47.24 | bright
70 | 20 | 41 | 19.7 | 2.89 | 45.89 | bright
70 | 30 | 41 | 19.67 | 2.92 | 46.28 | bright
70 | 40 | 41 | 19.64 | 2.92 | 46.19 | bright
70 | 50 | 41 | 19.67 | 3.08 | 48.81 | bright
70 | 60 | 41 | 19.51 | 2.94 | 46.15 | bright
70 | 70 | 41 | 19.4 | 2.85 | 44.65 | bright
70 | 80 | 41 | 19.42 | 1.69 | 26.38 | bright
70 | 90 | 41 | 19.2 | 1.18 | 18.18 | Bright

## Slide 17: The Result at 12.00 am (Dec 2009)
Angle N (°) | Angle S (°) | Temp (°C) | VOC (V) | ISC (A) | MPP (W) | Sky
0 | 0 | 50 | 19.73 | 2.73 | 43.40 | Bright
10 | 0 | 50 | 19.7 | 2.78 | 44.14 | Bright
20 | 0 | 50 | 19.67 | 2.8 | 44.38 | bright
30 | 0 | 50 | 19.64 | 2.82 | 44.61 | bright
40 | 0 | 50 | 19.64 | 2.8 | 44.29 | bright
50 | 0 | 50 | 19.64 | 2.87 | 45.40 | bright
60 | 0 | 50 | 19.76 | 3.32 | 52.88 | bright
70 | 0 | 50 | 19.7 | 2.96 | 47.00 | bright
80 | 0 | 50 | 19.6 | 2.89 | 45.63 | bright
90 | 0 | 50 | 19.4 | 2.8 | 43.87 | bright

## Slide 18: The Result at 12.00 am (Dec 2009)
Angle N (°) | Angle S (°) | Temp (°C) | VOC (V) | ISC (A) | MPP (W) | Sky
60 | 10 | 50 | 19.4 | 3.13 | 49.04 | bright
60 | 20 | 50 | 19.4 | 3.18 | 49.83 | bright
60 | 30 | 50 | 19.42 | 3.2 | 49.95 | bright
60 | 40 | 50 | 19.42 | 3.2 | 49.95 | bright
60 | 50 | 50 | 19.4 | 3.55 | 55.62 | bright
60 | 60 | 50 | 19.45 | 3.27 | 51.14 | bright
60 | 70 | 50 | 19.36 | 3.18 | 49.44 | bright
60 | 80 | 50 | 19.29 | 2.85 | 44.17 | bright
60 | 90 | 50 | 19 | 1.69 | 25.84 | bright

## Slide 19: Compilation of all Results (Dec 2009)
Time | W/O Reflector MPP (W) | With Reflector |  |  | Increase MPP
 |  | Angle N (°) | Angle S (°) | MPP (W) | 
09.00 | 36.74 | 70 | 50 | 48.81 | 132.85%
10.00 | 43.62 | 70 | 50 | 60.29 | 138.22%
11.00 | 35.41 | 70 | 60 | 47.83 | 135.07%
12.00 | 43.40 | 60 | 50 | 55.62 | 128.16%
13.00 | 42.23 | 70 | 50 | 49.91 | 118.19%
14.00 | 31.18 | 60 | 50 | 33.52 | 107.50%
15.00 | 21.41 | 70 | 40 | 22.34 | 104.34%
16.00 | 5.53 | 90 | 40 | 7.03 | 127.12%

## Slide 20: Conclusion
Double reflectors using common mirror as explained in this article has proved that it is able to increase the output of solar cell.
This method is relatively cheap and suitable for a country such Indonesia where there is no solar cell factory in the country. Yet the output of a solar cell can be increased by using mirrors.

## Slide 21: Conclusion
The measurement has neglected the effect of un-equal intensity of radiation on the surface of the solar cell. Because the solar cell is placed fixed horizontally, therefore during the morning and late afternoon the reflected sun-shine won’t fall at the whole surface of the solar cell completely. This phenomena is logically true when we saw the result of measurement.
By using this system which can be produced locally, one can increase the output of solar cell up to 23,93%.